| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Most Adverse | 25 | 6 mA | B |  | 85% |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 102.2 |
| Load Current: | None |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00715 |
| --- | --- |
| Shot 2 | 0.00635 |
| Shot 3 | 0.00719 |
| Shot 4 | 0.01220 |
| Shot 5 | 0.00817 |
| Shot 6 | 0.00840 |
| Shot 7 | 0.01960 |
| Shot 8 | 0.00733 |
| Shot 9 | 0.00668 |
| Shot 10 | 0.00447 |

Result:   Avg. Trip Time: 0.008754

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 2 | Most Adverse | 25 | 500 Ohm | B |  | 85% |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 102.1 |
| Load Current: | None |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 204 |

| Shot 1 | 0.00458 |
| --- | --- |
| Shot 2 | 0.00802 |
| Shot 3 | 0.00639 |
| Shot 4 | 0.01257 |
| Shot 5 | 0.00917 |
| Shot 6 | 0.01628 |
| Shot 7 | 0.00786 |
| Shot 8 | 0.01363 |
| Shot 9 | 0.01105 |
| Shot 10 | 0.00672 |

Result:   Avg. Trip Time: 0.009627

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 3 | Most Adverse | 25 | 6 mA | B |  | 100% |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | None |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.01356 |
| --- | --- |
| Shot 2 | 0.01046 |
| Shot 3 | 0.01976 |
| Shot 4 | 0.01184 |
| Shot 5 | 0.01956 |
| Shot 6 | 0.00622 |
| Shot 7 | 0.01063 |
| Shot 8 | 0.01964 |
| Shot 9 | 0.00891 |
| Shot 10 | 0.01835 |

Result:   Avg. Trip Time: 0.013893

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 4 | Most Adverse | 25 | 500 Ohm | B |  | 100% |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | None |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00724 |
| --- | --- |
| Shot 2 | 0.00725 |
| Shot 3 | 0.00730 |
| Shot 4 | 0.00448 |
| Shot 5 | 0.01155 |
| Shot 6 | 0.00597 |
| Shot 7 | 0.00748 |
| Shot 8 | 0.00521 |
| Shot 9 | 0.01499 |
| Shot 10 | 0.00796 |

Result:   Avg. Trip Time: 0.007943

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 5 | Most Adverse | 25 | 6 mA | B |  | 110% |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 132.2 |
| Load Current: | None |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.01110 |
| --- | --- |
| Shot 2 | 0.00751 |
| Shot 3 | 0.00859 |
| Shot 4 | 0.00396 |
| Shot 5 | 0.00814 |
| Shot 6 | 0.00612 |
| Shot 7 | 0.00942 |
| Shot 8 | 0.00938 |
| Shot 9 | 0.00864 |
| Shot 10 | 0.01624 |

Result:   Avg. Trip Time: 0.00891

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 6 | Most Adverse | 25 | 500 Ohm | B |  | 110% |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 132.1 |
| Load Current: | None |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 264 |

| Shot 1 | 0.00486 |
| --- | --- |
| Shot 2 | 0.01606 |
| Shot 3 | 0.00578 |
| Shot 4 | 0.01390 |
| Shot 5 | 0.01548 |
| Shot 6 | 0.00567 |
| Shot 7 | 0.00848 |
| Shot 8 | 0.00637 |
| Shot 9 | 0.01471 |
| Shot 10 | 0.01280 |

Result:   Avg. Trip Time: 0.010411

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 7 | Most Adverse | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Rated |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00968 |
| --- | --- |
| Shot 2 | 0.01268 |
| Shot 3 | 0.01414 |
| Shot 4 | 0.00481 |
| Shot 5 | 0.01898 |
| Shot 6 | 0.01890 |
| Shot 7 | 0.00707 |
| Shot 8 | 0.00710 |
| Shot 9 | 0.01902 |
| Shot 10 | 0.00510 |

Result:   Avg. Trip Time: 0.011748

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 8 | Most Adverse | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Rated |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01350 |
| --- | --- |
| Shot 2 | 0.00489 |
| Shot 3 | 0.01114 |
| Shot 4 | 0.00428 |
| Shot 5 | 0.01196 |
| Shot 6 | 0.00732 |
| Shot 7 | 0.01764 |
| Shot 8 | 0.00430 |
| Shot 9 | 0.00635 |
| Shot 10 | 0.00771 |

Result:   Avg. Trip Time: 0.008909

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 9 | Most Adverse | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | None |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00809 |
| --- | --- |
| Shot 2 | 0.00628 |
| Shot 3 | 0.00794 |
| Shot 4 | 0.01455 |
| Shot 5 | 0.00970 |
| Shot 6 | 0.01078 |
| Shot 7 | 0.01200 |
| Shot 8 | 0.00764 |
| Shot 9 | 0.01437 |
| Shot 10 | 0.00661 |

Result:   Avg. Trip Time: 0.009796

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 10 | Most Adverse | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | None |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00449 |
| --- | --- |
| Shot 2 | 0.01527 |
| Shot 3 | 0.00564 |
| Shot 4 | 0.00783 |
| Shot 5 | 0.00751 |
| Shot 6 | 0.01143 |
| Shot 7 | 0.00424 |
| Shot 8 | 0.01020 |
| Shot 9 | 0.00433 |
| Shot 10 | 0.00660 |

Result:   Avg. Trip Time: 0.007754

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 11 | Most Adverse | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.01411 |
| --- | --- |
| Shot 2 | 0.01788 |
| Shot 3 | 0.00438 |
| Shot 4 | 0.01890 |
| Shot 5 | 0.00558 |
| Shot 6 | 0.01586 |
| Shot 7 | 0.01397 |
| Shot 8 | 0.01878 |
| Shot 9 | 0.01199 |
| Shot 10 | 0.01202 |

Result:   Avg. Trip Time: 0.013347

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 12 | Most Adverse | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Forward |
| Position: | 1 |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00628 |
| --- | --- |
| Shot 2 | 0.00448 |
| Shot 3 | 0.01250 |
| Shot 4 | 0.01114 |
| Shot 5 | 0.01722 |
| Shot 6 | 0.00829 |
| Shot 7 | 0.01383 |
| Shot 8 | 0.01244 |
| Shot 9 | 0.01256 |
| Shot 10 | 0.00502 |

Result:   Avg. Trip Time: 0.010376

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 13 | Most Adverse | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Reverse |
| Position: | 1 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00880 |
| --- | --- |
| Shot 2 | 0.01050 |
| Shot 3 | 0.00742 |
| Shot 4 | 0.02350 |
| Shot 5 | 0.03785 |
| Shot 6 | 0.03706 |
| Shot 7 | 0.03590 |
| Shot 8 | 0.03534 |
| Shot 9 | 0.01007 |
| Shot 10 | 0.01523 |

Result:   Avg. Trip Time: 0.022167

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 14 | Most Adverse | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Reverse |
| Position: | 1 |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01002 |
| --- | --- |
| Shot 2 | 0.00453 |
| Shot 3 | 0.01199 |
| Shot 4 | 0.00645 |
| Shot 5 | 0.01034 |
| Shot 6 | 0.00708 |
| Shot 7 | 0.01120 |
| Shot 8 | 0.01452 |
| Shot 9 | 0.00466 |
| Shot 10 | 0.01228 |

Result:   Avg. Trip Time: 0.009307

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 15 | Most Adverse | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 1 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00755 |
| --- | --- |
| Shot 2 | 0.03677 |
| Shot 3 | 0.01310 |
| Shot 4 | 0.00901 |
| Shot 5 | 0.01050 |
| Shot 6 | 0.03736 |
| Shot 7 | 0.00814 |
| Shot 8 | 0.03660 |
| Shot 9 | 0.02441 |
| Shot 10 | 0.03900 |

Result:   Avg. Trip Time: 0.022244

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 16 | Most Adverse | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 1 |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01284 |
| --- | --- |
| Shot 2 | 0.00679 |
| Shot 3 | 0.00623 |
| Shot 4 | 0.00622 |
| Shot 5 | 0.01591 |
| Shot 6 | 0.00523 |
| Shot 7 | 0.00700 |
| Shot 8 | 0.01116 |
| Shot 9 | 0.01615 |
| Shot 10 | 0.01349 |

Result:   Avg. Trip Time: 0.010102

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 17 | Most Adverse | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 2 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.03709 |
| --- | --- |
| Shot 2 | 0.04035 |
| Shot 3 | 0.02442 |
| Shot 4 | 0.04138 |
| Shot 5 | 0.00790 |
| Shot 6 | 0.00863 |
| Shot 7 | 0.01204 |
| Shot 8 | 0.03633 |
| Shot 9 | 0.01114 |
| Shot 10 | 0.03984 |

Result:   Avg. Trip Time: 0.025912

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 18 | Most Adverse | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 2 |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01110 |
| --- | --- |
| Shot 2 | 0.00798 |
| Shot 3 | 0.01317 |
| Shot 4 | 0.00948 |
| Shot 5 | 0.00646 |
| Shot 6 | 0.01336 |
| Shot 7 | 0.00537 |
| Shot 8 | 0.00477 |
| Shot 9 | 0.00533 |
| Shot 10 | 0.00797 |

Result:   Avg. Trip Time: 0.008499

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 19 | Most Adverse | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 3 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.01115 |
| --- | --- |
| Shot 2 | 0.00957 |
| Shot 3 | 0.01707 |
| Shot 4 | 0.00857 |
| Shot 5 | 0.00766 |
| Shot 6 | 0.04044 |
| Shot 7 | 0.00810 |
| Shot 8 | 0.00831 |
| Shot 9 | 0.01092 |
| Shot 10 | 0.03899 |

Result:   Avg. Trip Time: 0.016078

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 20 | Most Adverse | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 3 |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00484 |
| --- | --- |
| Shot 2 | 0.01608 |
| Shot 3 | 0.01396 |
| Shot 4 | 0.00648 |
| Shot 5 | 0.01033 |
| Shot 6 | 0.01355 |
| Shot 7 | 0.00673 |
| Shot 8 | 0.00983 |
| Shot 9 | 0.00886 |
| Shot 10 | 0.00461 |

Result:   Avg. Trip Time: 0.009527

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 21 | Most Adverse | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 4 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.01008 |
| --- | --- |
| Shot 2 | 0.03905 |
| Shot 3 | 0.00759 |
| Shot 4 | 0.01126 |
| Shot 5 | 0.03848 |
| Shot 6 | 0.03726 |
| Shot 7 | 0.01702 |
| Shot 8 | 0.01068 |
| Shot 9 | 0.01158 |
| Shot 10 | 0.03855 |

Result:   Avg. Trip Time: 0.022155

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 22 | Most Adverse | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 4 |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01482 |
| --- | --- |
| Shot 2 | 0.01210 |
| Shot 3 | 0.00754 |
| Shot 4 | 0.01027 |
| Shot 5 | 0.01014 |
| Shot 6 | 0.00687 |
| Shot 7 | 0.00601 |
| Shot 8 | 0.01203 |
| Shot 9 | 0.01375 |
| Shot 10 | 0.01294 |

Result:   Avg. Trip Time: 0.010647

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 23 | Most Adverse | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 5 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.02155 |
| --- | --- |
| Shot 2 | 0.01073 |
| Shot 3 | 0.03782 |
| Shot 4 | 0.01720 |
| Shot 5 | 0.01283 |
| Shot 6 | 0.04009 |
| Shot 7 | 0.00962 |
| Shot 8 | 0.01033 |
| Shot 9 | 0.00849 |
| Shot 10 | 0.00795 |

Result:   Avg. Trip Time: 0.017661

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 24 | Most Adverse | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 5 |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01397 |
| --- | --- |
| Shot 2 | 0.00809 |
| Shot 3 | 0.01420 |
| Shot 4 | 0.00458 |
| Shot 5 | 0.01086 |
| Shot 6 | 0.00462 |
| Shot 7 | 0.01519 |
| Shot 8 | 0.00776 |
| Shot 9 | 0.00454 |
| Shot 10 | 0.00781 |

Result:   Avg. Trip Time: 0.009162

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 25 | Most Adverse | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 6 |
| Metered Rb Current: | 6 |

| Shot 1 | 0.03713 |
| --- | --- |
| Shot 2 | 0.00968 |
| Shot 3 | 0.01765 |
| Shot 4 | 0.01214 |
| Shot 5 | 0.03670 |
| Shot 6 | 0.00805 |
| Shot 7 | 0.04038 |
| Shot 8 | 0.04041 |
| Shot 9 | 0.00853 |
| Shot 10 | 0.01307 |

Result:   Avg. Trip Time: 0.022374

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 26 | Most Adverse | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | 6 |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00453 |
| --- | --- |
| Shot 2 | 0.01491 |
| Shot 3 | 0.01050 |
| Shot 4 | 0.01224 |
| Shot 5 | 0.01286 |
| Shot 6 | 0.00922 |
| Shot 7 | 0.01619 |
| Shot 8 | 0.00697 |
| Shot 9 | 0.01219 |
| Shot 10 | 0.00463 |

Result:   Avg. Trip Time: 0.010424

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 28 | Calibration | 25 | 6 mA | A |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.01502 |
| --- | --- |
| Shot 2 | 0.00069 |
| Shot 3 | 0.00053 |
| Shot 4 | 0.00136 |
| Shot 5 | 0.00024 |
| Shot 6 | 0.00045 |
| Shot 7 | 0.01397 |
| Shot 8 | 0.00139 |
| Shot 9 | 0.00501 |
| Shot 10 | 0.01950 |

Result:   Avg. Trip Time: 0.005816

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 29 | Calibration | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.01424 |
| --- | --- |
| Shot 2 | 0.00840 |
| Shot 3 | 0.01105 |
| Shot 4 | 0.04033 |
| Shot 5 | 0.01075 |
| Shot 6 | 0.00913 |
| Shot 7 | 0.03706 |
| Shot 8 | 0.01196 |
| Shot 9 | 0.04016 |
| Shot 10 | 0.03595 |

Result:   Avg. Trip Time: 0.021903

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 30 | Calibration | 25 | 6 mA | C |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00348 |
| --- | --- |
| Shot 2 | 0.01263 |
| Shot 3 | 0.01664 |
| Shot 4 | 0.00350 |
| Shot 5 | 0.00815 |
| Shot 6 | 0.01148 |
| Shot 7 | 0.01619 |
| Shot 8 | 0.00559 |
| Shot 9 | 0.00836 |
| Shot 10 | 0.00944 |

Result:   Avg. Trip Time: 0.009546

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 31 | Calibration | 25 | 6 mA | D |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00981 |
| --- | --- |
| Shot 2 | 0.00990 |
| Shot 3 | 0.00562 |
| Shot 4 | 0.01486 |
| Shot 5 | 0.01806 |
| Shot 6 | 0.00373 |
| Shot 7 | 0.00957 |
| Shot 8 | 0.01424 |
| Shot 9 | 0.01692 |
| Shot 10 | 0.01842 |

Result:   Avg. Trip Time: 0.012113

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 32 | Calibration | 25 | 500 Ohm | A |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00050 |
| --- | --- |
| Shot 2 | 0.00687 |
| Shot 3 | 0.00036 |
| Shot 4 | 0.00683 |
| Shot 5 | 0.00131 |
| Shot 6 | 0.00024 |
| Shot 7 | 0.00578 |
| Shot 8 | 0.00042 |
| Shot 9 | 0.00066 |
| Shot 10 | 0.00030 |

Result:   Avg. Trip Time: 0.002327

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 33 | Calibration | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01362 |
| --- | --- |
| Shot 2 | 0.00469 |
| Shot 3 | 0.00908 |
| Shot 4 | 0.00476 |
| Shot 5 | 0.00476 |
| Shot 6 | 0.00539 |
| Shot 7 | 0.00537 |
| Shot 8 | 0.00919 |
| Shot 9 | 0.00628 |
| Shot 10 | 0.00537 |

Result:   Avg. Trip Time: 0.006851

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 34 | Calibration | 25 | 500 Ohm | C |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00352 |
| --- | --- |
| Shot 2 | 0.00007 |
| Shot 3 | 0.00654 |
| Shot 4 | 0.00476 |
| Shot 5 | 0.00672 |
| Shot 6 | 0.01117 |
| Shot 7 | 0.00451 |
| Shot 8 | 0.00402 |
| Shot 9 | 0.01129 |
| Shot 10 | 0.00339 |

Result:   Avg. Trip Time: 0.005599

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 35 | Calibration | 25 | 500 Ohm | D |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01399 |
| --- | --- |
| Shot 2 | 0.01743 |
| Shot 3 | 0.01390 |
| Shot 4 | 0.01354 |
| Shot 5 | 0.01053 |
| Shot 6 | 0.01790 |
| Shot 7 | 0.01523 |
| Shot 8 | 0.00532 |
| Shot 9 | 0.00809 |
| Shot 10 | 0.00947 |

Result:   Avg. Trip Time: 0.01254

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 36 | Calibration | 25 | 1200 Ohm | A |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 100 |

| Shot 1 | 0.00046 |
| --- | --- |
| Shot 2 | 0.00336 |
| Shot 3 | 0.00020 |
| Shot 4 | 0.00301 |
| Shot 5 | 0.00028 |
| Shot 6 | 0.00051 |
| Shot 7 | 0.00024 |
| Shot 8 | 0.00909 |
| Shot 9 | 0.00066 |
| Shot 10 | 0.00059 |

Result:   Avg. Trip Time: 0.00184

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 37 | Calibration | 25 | 1200 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 100 |

| Shot 1 | 0.00723 |
| --- | --- |
| Shot 2 | 0.00633 |
| Shot 3 | 0.01410 |
| Shot 4 | 0.00494 |
| Shot 5 | 0.00624 |
| Shot 6 | 0.00498 |
| Shot 7 | 0.01244 |
| Shot 8 | 0.00585 |
| Shot 9 | 0.00472 |
| Shot 10 | 0.00468 |

Result:   Avg. Trip Time: 0.007151

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 38 | Calibration | 25 | 1200 Ohm | C |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 100 |

| Shot 1 | 0.01118 |
| --- | --- |
| Shot 2 | 0.00401 |
| Shot 3 | 0.00788 |
| Shot 4 | 0.00320 |
| Shot 5 | 0.00740 |
| Shot 6 | 0.01418 |
| Shot 7 | 0.00358 |
| Shot 8 | 0.00669 |
| Shot 9 | 0.01321 |
| Shot 10 | 0.00941 |

Result:   Avg. Trip Time: 0.008074

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 39 | Calibration | 25 | 1200 Ohm | D |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 100 |

| Shot 1 | 0.00745 |
| --- | --- |
| Shot 2 | 0.01702 |
| Shot 3 | 0.01165 |
| Shot 4 | 0.01687 |
| Shot 5 | 0.00715 |
| Shot 6 | 0.00765 |
| Shot 7 | 0.01378 |
| Shot 8 | 0.01280 |
| Shot 9 | 0.00742 |
| Shot 10 | 0.00755 |

Result:   Avg. Trip Time: 0.010934

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 61 | Calibration | 66 | 6 mA | A |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.01277 |
| --- | --- |
| Shot 2 | 0.00355 |
| Shot 3 | 0.02025 |
| Shot 4 | 0.01690 |
| Shot 5 | 0.00673 |
| Shot 6 | 0.00090 |
| Shot 7 | 0.01960 |
| Shot 8 | 0.01004 |
| Shot 9 | 0.01840 |
| Shot 10 | 0.01020 |

Result:   Avg. Trip Time: 0.011934

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 62 | Calibration | 66 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00937 |
| --- | --- |
| Shot 2 | 0.01131 |
| Shot 3 | 0.01115 |
| Shot 4 | 0.00705 |
| Shot 5 | 0.01397 |
| Shot 6 | 0.01172 |
| Shot 7 | 0.02092 |
| Shot 8 | 0.01303 |
| Shot 9 | 0.01837 |
| Shot 10 | 0.01210 |

Result:   Avg. Trip Time: 0.012899

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 63 | Calibration | 66 | 6 mA | C |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00979 |
| --- | --- |
| Shot 2 | 0.01700 |
| Shot 3 | 0.01212 |
| Shot 4 | 0.00536 |
| Shot 5 | 0.01484 |
| Shot 6 | 0.00727 |
| Shot 7 | 0.00377 |
| Shot 8 | 0.01150 |
| Shot 9 | 0.01022 |
| Shot 10 | 0.01067 |

Result:   Avg. Trip Time: 0.010254

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 64 | Calibration | 66 | 6 mA | D |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00502 |
| --- | --- |
| Shot 2 | 0.01520 |
| Shot 3 | 0.01623 |
| Shot 4 | 0.01106 |
| Shot 5 | 0.00670 |
| Shot 6 | 0.00551 |
| Shot 7 | 0.01515 |
| Shot 8 | 0.01206 |
| Shot 9 | 0.01790 |
| Shot 10 | 0.00755 |

Result:   Avg. Trip Time: 0.011238

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 65 | Calibration | 66 | 500 Ohm | A |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00042 |
| --- | --- |
| Shot 2 | 0.01870 |
| Shot 3 | 0.01885 |
| Shot 4 | 0.00417 |
| Shot 5 | 0.00162 |
| Shot 6 | 0.00013 |
| Shot 7 | 0.00335 |
| Shot 8 | 0.00063 |
| Shot 9 | 0.00283 |
| Shot 10 | 0.00027 |

Result:   Avg. Trip Time: 0.005097

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 66 | Calibration | 66 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01117 |
| --- | --- |
| Shot 2 | 0.00644 |
| Shot 3 | 0.00474 |
| Shot 4 | 0.00466 |
| Shot 5 | 0.01426 |
| Shot 6 | 0.00628 |
| Shot 7 | 0.01599 |
| Shot 8 | 0.00680 |
| Shot 9 | 0.00508 |
| Shot 10 | 0.01962 |

Result:   Avg. Trip Time: 0.009504

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 67 | Calibration | 66 | 500 Ohm | C |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01344 |
| --- | --- |
| Shot 2 | 0.01336 |
| Shot 3 | 0.00393 |
| Shot 4 | 0.00518 |
| Shot 5 | 0.00942 |
| Shot 6 | 0.00514 |
| Shot 7 | 0.00593 |
| Shot 8 | 0.01312 |
| Shot 9 | 0.00582 |
| Shot 10 | 0.01020 |

Result:   Avg. Trip Time: 0.008554

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 68 | Calibration | 66 | 500 Ohm | D |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00512 |
| --- | --- |
| Shot 2 | 0.00806 |
| Shot 3 | 0.00560 |
| Shot 4 | 0.01140 |
| Shot 5 | 0.01579 |
| Shot 6 | 0.01052 |
| Shot 7 | 0.00612 |
| Shot 8 | 0.01099 |
| Shot 9 | 0.00540 |
| Shot 10 | 0.01254 |

Result:   Avg. Trip Time: 0.009154

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 91 | Calibration | -35 | 6 mA | A |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 0 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 0 |

| Shot 1 | 0.00135 |
| --- | --- |
| Shot 2 | 0.00131 |
| Shot 3 | 0.01733 |
| Shot 4 | 0.01845 |
| Shot 5 | 0.01147 |
| Shot 6 | 0.02098 |
| Shot 7 | 0.01833 |
| Shot 8 | 0.02362 |
| Shot 9 | 0.00000 |
| Shot 10 | 6.00000 |

Result:   Avg. Trip Time: 0

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 92 | Calibration | -35 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.01958 |
| --- | --- |
| Shot 2 | 0.01838 |
| Shot 3 | 0.01370 |
| Shot 4 | 0.01729 |
| Shot 5 | 0.01441 |
| Shot 6 | 0.02236 |
| Shot 7 | 0.01097 |
| Shot 8 | 0.02015 |
| Shot 9 | 0.01140 |
| Shot 10 | 0.01730 |

Result:   Avg. Trip Time: 0.016554

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 93 | Calibration | -35 | 6 mA | C |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.01210 |
| --- | --- |
| Shot 2 | 0.00345 |
| Shot 3 | 0.00760 |
| Shot 4 | 0.00356 |
| Shot 5 | 0.00558 |
| Shot 6 | 0.00880 |
| Shot 7 | 0.01453 |
| Shot 8 | 0.00412 |
| Shot 9 | 0.00652 |
| Shot 10 | 0.01611 |

Result:   Avg. Trip Time: 0.008237

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 94 | Calibration | -35 | 6 mA | D |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00382 |
| --- | --- |
| Shot 2 | 0.01037 |
| Shot 3 | 0.00576 |
| Shot 4 | 0.00634 |
| Shot 5 | 0.01884 |
| Shot 6 | 0.01184 |
| Shot 7 | 0.01060 |
| Shot 8 | 0.01717 |
| Shot 9 | 0.00510 |
| Shot 10 | 0.01732 |

Result:   Avg. Trip Time: 0.010716

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 95 | Calibration | -35 | 500 Ohm | A |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: |  |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: |  |

| Shot 1 | 0.00128 |
| --- | --- |
| Shot 2 | 0.00840 |
| Shot 3 | 0.00001 |
| Shot 4 | 0.00036 |
| Shot 5 | 0.00090 |
| Shot 6 | 0.00582 |
| Shot 7 | 0.00012 |
| Shot 8 | 0.00000 |
| Shot 9 | 240.00000 |
| Shot 10 | 0.00000 |

Result:   Avg. Trip Time: 0

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 96 | Calibration | -35 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00416 |
| --- | --- |
| Shot 2 | 0.01426 |
| Shot 3 | 0.00722 |
| Shot 4 | 0.00763 |
| Shot 5 | 0.00424 |
| Shot 6 | 0.01028 |
| Shot 7 | 0.00782 |
| Shot 8 | 0.01430 |
| Shot 9 | 0.01125 |
| Shot 10 | 0.01516 |

Result:   Avg. Trip Time: 0.009632

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 97 | Calibration | -35 | 500 Ohm | C |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01331 |
| --- | --- |
| Shot 2 | 0.01063 |
| Shot 3 | 0.00322 |
| Shot 4 | 0.01126 |
| Shot 5 | 0.01162 |
| Shot 6 | 0.01025 |
| Shot 7 | 0.01010 |
| Shot 8 | 0.00330 |
| Shot 9 | 0.00746 |
| Shot 10 | 0.01561 |

Result:   Avg. Trip Time: 0.009676

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 98 | Calibration | -35 | 500 Ohm | D |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01470 |
| --- | --- |
| Shot 2 | 0.01327 |
| Shot 3 | 0.01679 |
| Shot 4 | 0.01147 |
| Shot 5 | 0.01248 |
| Shot 6 | 0.01576 |
| Shot 7 | 0.01834 |
| Shot 8 | 0.01352 |
| Shot 9 | 0.01218 |
| Shot 10 | 0.00666 |

Result:   Avg. Trip Time: 0.013517

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 120 | Calibration | 25 | 6 mA | A |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.01741 |
| --- | --- |
| Shot 2 | 0.01884 |
| Shot 3 | 0.01210 |
| Shot 4 | 0.00034 |
| Shot 5 | 0.01814 |
| Shot 6 | 0.00066 |
| Shot 7 | 0.01698 |
| Shot 8 | 0.01964 |
| Shot 9 | 0.01592 |
| Shot 10 | 0.00033 |

Result:   Avg. Trip Time: 0.012036

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 121 | Calibration | 25 | 6 mA | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.02280 |
| --- | --- |
| Shot 2 | 0.01399 |
| Shot 3 | 0.00696 |
| Shot 4 | 0.00796 |
| Shot 5 | 0.01961 |
| Shot 6 | 0.01649 |
| Shot 7 | 0.01408 |
| Shot 8 | 0.01619 |
| Shot 9 | 0.01733 |
| Shot 10 | 0.00825 |

Result:   Avg. Trip Time: 0.014366

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 122 | Calibration | 25 | 6 mA | C |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00498 |
| --- | --- |
| Shot 2 | 0.01281 |
| Shot 3 | 0.00355 |
| Shot 4 | 0.00675 |
| Shot 5 | 0.00648 |
| Shot 6 | 0.01437 |
| Shot 7 | 0.00548 |
| Shot 8 | 0.01196 |
| Shot 9 | 0.00376 |
| Shot 10 | 0.01524 |

Result:   Avg. Trip Time: 0.008538

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 123 | Calibration | 25 | 6 mA | D |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 6 |

| Shot 1 | 0.00930 |
| --- | --- |
| Shot 2 | 0.00423 |
| Shot 3 | 0.01510 |
| Shot 4 | 0.00910 |
| Shot 5 | 0.01651 |
| Shot 6 | 0.00657 |
| Shot 7 | 0.01084 |
| Shot 8 | 0.01136 |
| Shot 9 | 0.01459 |
| Shot 10 | 0.00670 |

Result:   Avg. Trip Time: 0.01043

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 124 | Calibration | 25 | 500 Ohm | A |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00010 |
| --- | --- |
| Shot 2 | 0.00015 |
| Shot 3 | 0.00037 |
| Shot 4 | 0.00023 |
| Shot 5 | 0.01153 |
| Shot 6 | 0.00050 |
| Shot 7 | 0.00052 |
| Shot 8 | 0.00023 |
| Shot 9 | 0.00343 |
| Shot 10 | 0.00023 |

Result:   Avg. Trip Time: 0.001729

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 125 | Calibration | 25 | 500 Ohm | B |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.2 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.01514 |
| --- | --- |
| Shot 2 | 0.00471 |
| Shot 3 | 0.01211 |
| Shot 4 | 0.01318 |
| Shot 5 | 0.00528 |
| Shot 6 | 0.00463 |
| Shot 7 | 0.00859 |
| Shot 8 | 0.00460 |
| Shot 9 | 0.01019 |
| Shot 10 | 0.00530 |

Result:   Avg. Trip Time: 0.008373

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 126 | Calibration | 25 | 500 Ohm | C |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00320 |
| --- | --- |
| Shot 2 | 0.00393 |
| Shot 3 | 0.01246 |
| Shot 4 | 0.00628 |
| Shot 5 | 0.00314 |
| Shot 6 | 0.00317 |
| Shot 7 | 0.00599 |
| Shot 8 | 0.01393 |
| Shot 9 | 0.00314 |
| Shot 10 | 0.00613 |

Result:   Avg. Trip Time: 0.006137

| Line | Test Mode | Temperature | Fault | Switch Mode | Parameter | Line Voltage |
| --- | --- | --- | --- | --- | --- | --- |
| 127 | Calibration | 25 | 500 Ohm | D |  | Most Adverse |

| Test Conditions At: | {{TestConditionsAt}} |
| --- | --- |
| Voltage: | 120.1 |
| Load Current: | Most Adverse |
| Polarity: | Most Adverse |
| Position: | Most Adverse |
| Metered Rb Current: | 240 |

| Shot 1 | 0.00666 |
| --- | --- |
| Shot 2 | 0.00609 |
| Shot 3 | 0.01549 |
| Shot 4 | 0.00776 |
| Shot 5 | 0.01238 |
| Shot 6 | 0.00442 |
| Shot 7 | 0.01534 |
| Shot 8 | 0.01066 |
| Shot 9 | 0.00434 |
| Shot 10 | 0.00763 |

Result:   Avg. Trip Time: 0.009077